## Slide 1: Ventilation and modular HVAC systems
MORE-CONENCT 4th training module
Duration: 4 hours
Type: class room lectures
Dr.sc.ing. Anatolijs Borodiņecs

## Slide 2: Introduction
As the buildings are built for people not to consume/save energy it is vitally important also for nZEB to provide comfortable and non-harmful indoor air parameters for occupants. This usually involves designing and installing various HVAC systems. Just in case of nZEB the added challenge of keeping the energy consumption as low as possible comes into play.
The primary objective of this learning module is to give information and present study results on how to evaluate possible heating, ventilation and air-conditioning solutions for nZEB multi apartment buildings.
In scope of this module technology inventory and review of all necessary components that are necessary to climatize the buildings will be evaluated. A specific focus will be paid to modular solutions. The design specifics of embedded ventilation ducts and modular energy unit will also analyzed.
The ventilation norms and guidelines for MORE-CONENCT project countries will be compared and discussed. The module will summarize a brief overview of different ventilation systems advantages and disadvantages. It will provide comparison of installation and running costs for various ventilation solution for Latvian case study.
After completing this module individuals will be able to choose ventilation strategy considering building type, technical conditions and user behavior. Also knowledge on duct sizing and selection of ventilation units will be obtained.

## Slide 3: Ventilation systems
Ventilation is one of the most complex systems as it has many possible solutions and variations. However it is one of the most important systems as it provides fresh air and in many cases is the main reason for bad IAQ and cause of Sick Building Syndrome.
The ventilation systems can be dived in three large groups according to types:
  natural ventilation,
  hybrid ventilation (mechanical exhaust ventilation),
  mechanical supply-exhaust ventilation
    Apartment based ventilation system
    Building based ventilation system

## Slide 4: Learning tasks and methodology
To evaluate possible ventilation solutions for nZEB multi apartment buildings in three European geoclusters
To perform economic and technical comparison of different ventilation systems
To develop introduction of modular solutions and integration of ventilation ducts into external insulation
Determining the necessary ventilation air volumes in case of each country;
Designing most common ventilation system types for an apartment;
Estimating construction costs of ventilation system installing;
Calculating and comparing the life cycle costs of each ventilation system including maintenance, necessary electrical energy and necessary energy for heating;
Estimating practical solutions for integration of ventilation systems elements into limited technical space available in exiting post-war multi apartment buildings;

## Slide 5: Geo-cluster concept
Geo-cluster concept illustrates trans-national areas where strong similarities are found in terms of climate, culture, construction typologies and other factors. During this paper the focus will be on GC 1 represented by Denmark, GC2 represented by Estonia and Latvia and GC4 represented by Portugal.
Fig. 1. EU H2020 MORE-CONNECT project geo-cluster

## Slide 6: Ventilation air calculation
Table 1. Necessary residential ventilation airflow rates according to local regulations
Room type | Unit | Geo-clusters and countries* |  |  | 
 |  | GC1 | GC2 | GC2 | GC4
 |  | Denmark | Estonia | Latvia | Portugal
Toilet | m3/h | 36 | 36 | 25 | 30 to 60
Bathroom with toilet | m3/h | 54 | 54 | 50 | 45 to 90
Staircases | m3/(h·m2) | 1.08 | 1.25 | 1 | n/a
Bedroom | m3/(h·m2) | 1.08 | 12 l/s (8 l/s in <11m2 bedroom) | 3 | Dependent on room size. Approximate value is 1h-1
Kitchen | m3/h | 72 | 30 (22 for 1 room apartment)** | 60-90 | 60 to 120
Hallway | h-1 | 0.5 | - | 0.5 - 1 | n/a
Technical room | h-1 | 0.5 | 0.5 | 0.5 - 1 | -
Total supply air | m3/(h·m2) | 1.08 | 1.5 | - | The sum of the supply air of all bedrooms and living rooms
Latvia – 4200 m3/h; Denmark – 1250 m3/; Estonia – 2745 m3/h; Portugal – 4050 m3/h

## Slide 7: Ventilation air calculation (2)
Calculated ventilation air volumes for Latvian case study building
Room nr. | Room type | Supply air m3/h | Exhaust air m3/h
1 | Bedroom | 55 (90 for 2-room apartment) | -
2 | Kitchen | - | 90
3 | Bathroom | - | 50
4 | Storage | - | -
Total for an apartment (m3/h) |  | 55 (90) | 140
Total for whole building (m3/h) |  | 6 · 5 · 140 = 4200 | 
Room nr. | Room type | Supply air m3/h | Exhaust air m3/h
1 | Bedroom | 86* | -
2 | Kitchen | - | 22 (30 for 2-room apartment)
3 | Bathroom+WC | - | 54
4 | Storage | - | 10
Total for an apartment (m3/h) |  | 86* | 86
Total for whole building (m3/h) |  | (5 · 86 + 119) · 5=2745 | 
Calculated ventilation air volumes for Ėstonian case study building
Room nr. | Room type | Supply air m3/h | Exhaust air m3/h
1 | Bedroom | 20 | 
2 | Kitchen | - | 72 - VAV
3 | Bathroom | - | 54 - VAV
4 | Storage | - | -
Total for an apartment (m3/h) |  | 40 (50)* | 40 (50)*
Total for whole building (m3/h) |  | (5 · 40 + 50) · 5 = 1250 | 
Calculated ventilation air volumes for Denmark case study building
Fig. 2. (a) Plan of 1-room apartment of case building; (b) Plan of whole staircase section of case study building

## Slide 8: Ventilation type selection (1)
Ventilation system through openable windows and natural exhaust
Ventilation system through air inlets and natural exhaust
Name | Size | Units | Quantity | Average price in EU for one unit (EUR)
Extract grille | 200x100 mm | Pcs. | 1 | 17.00
Extract grille | 200x200 mm | Pcs. | 1 | 20.00
Duct | Ø200 mm | m | 2 | 1.90
Duct | Ø160 mm | m | 3 | 1.50
Total cost with 30 % added |  |  |  | 60.00
Name | Size | Units | Quantity | Average price in EU for one unit (EUR)
Supply vents | Ø160 mm | Pcs. | 2 | 120.00
Extract grille | 200x100 mm | Pcs. | 1 | 17.00
Extract grille | 200x200 mm | Pcs. | 1 | 20.00
Duct | Ø200 mm | m | 2 | 1.90
Duct | Ø160 mm | m | 3 | 1.50
Total cost with 30 % added |  |  |  | 370.00

## Slide 9: Ventilation type selection (2)
Hybrid type ventilation system with supply through air inlets and mechanical exhaust
Decentralized ventilation system with room based mechanical supply and exhaust with room based heat recovery
Name | Size | Units | Quantity | Average price in EU for one unit (EUR)
Supply vents | Ø160 mm | Pcs. | 2 | 120.00
Domestic type extract fan | Ø100 mm | Pcs. | 1 | 70.00
Domestic type extract fan | Ø200 mm | Pcs. | 1 | 90.00
Duct | Ø125 mm | m | 2 | 1.20
Duct | Ø100 mm | m | 3 | 0.90
Total cost with 30 % added |  |  |  | 525.00
Name | Size | Units | Quantity | Average price in EU for one unit (EUR)
Paired decentralized ventilation devices (50 and 90 m3/h) | - | Pcs. | 4 | 485.00
Control unit | - | Pcs. | 1 | 320
Domestic type extract fan | Ø100 mm | Pcs. | 1 | 70.00
Duct | Ø100 mm | m | 2 | 0.90
Total cost with 10 % added |  |  |  | 2560.00

## Slide 10: Ventilation type selection (3)
High-tech ceramic energy accumulator with regenerating efficiency up to 90%
Reversible EC ventilator with low energy demand from 3.5 up to 6.1 W and safe voltage 12 V
Cena ap 350 EUR gabalā

## Slide 11: Ventilation type selection (4)
Decentralized ventilation system with apartment based mechanical supply and exhaust with apartment based heat recovery
Centralized ventilation system with building based mechanical supply and exhaust with heat recovery
Name | Size | Units | Quantity | Average price in EU for one unit (EUR)
AHU (140 m3/h) | - | Pcs. | 1 | 1800.00
Air intake grill | 200x200 mm | Pcs. | 1 | 40.00
Extract air roof hood | Ø160 mm | Pcs. | 1 | 200.00
Air supply grill | 200x100 mm | Pcs. | 2 | 17.00
Air exhaust grill | 200x100 mm | Pcs. | 1 | 17.00
Air exhaust valve | Ø100 | Pcs. | 1 | 5.00
Duct | Ø160 mm | m | 10 | 1.50
Duct | Ø125 mm | m | 4 | 1.20
Duct | Ø100 mm | m | 7 | 0.90
Silencers | Ø100 mm/ L=1000mm | Pcs. | 4 | 75.00
Total cost with 20 % added |  |  |  | 2900.00
Name | Size | Units | Quantity | Average price in EU for one unit (EUR)
For whole building |  |  |  | 
Centralized AHU (4200 m3/h) | - | Pcs. | 1 | 9500.00
Air intake grill | Ø560 mm | Pcs. | 1 | 100.00
Extract air roof hood | Ø560 mm | Pcs. | 1 | 700.00
Silencers | Ø560 mm/ L=1000mm | Pcs. | 4 | 250.00
Duct | Ø560 mm | m | 20 | 17.30
For apartment |  |  |  | 
Air supply valve | Ø100 mm | Pcs. | 2 | 5.00
Air exhaust grill | 200x100 mm | Pcs. | 1 | 17.00
Air exhaust valve | Ø100 mm | Pcs. | 1 | 5.00
Duct | Ø160 mm | m | 3 | 1.50
Duct | Ø125 mm | m | 4 | 1.20
Total cost with 30 % added* |  |  |  | 560.00
*The total cost includes the cost of all units located in the apartment and 1/30 of whole price for whole building units, as there are thirty apartments that would be served by the AHU.

## Slide 12: Life cycle cost analysis
Type of ventilation system | Installation costs1) (EUR) | Maintenance costs2) (EUR) | Heating costs3) (EUR) | Powering costs4) (EUR) | Total Annual costs (EUR)
Natural by opening windows and natural exhaust | 1800 | - - | 8005 8110 | - - | 8005 8110
Natural by having inlet valves and natural exhaust | 11 100 | 300 450 | 8005 8110 | - - | 8305 8560
Hybrid by having inlet devices in walls and mechanical exhaust | 15 750 | 450 600 | 8005 8110 | 1155 1025 | 9610 9465
Decentralized mechanical supply and exhaust with heat recovery (room based system) | 76 800 | 750 750 | 1600 (eff. 0,80) 1620 (eff. 0,8) | 535 580 (0,16 W/m3/h) | 2885 2950
Decentralized mechanical supply and exhaust with heat recovery (apartment based system) | 87 000 | 1050 1500 | 1200 (eff. 0,85) 2030 (eff. 0,75) | 3455 (SFP 1.0) 3210 (SFP 1.6) | 5705 6740
Centralized mechanical supply and exhaust with heat recovery | 16 760 | 1000 1000 | 1600 (eff. 0,80) 2030 (eff. 0,75) | 2070 (SFP 1.2) 4010 (SFP 2.0) | 4670 7040
Comparison of installation and running costs for Latvian / Estonian case study (upper numbers are for Latvia, lower for Estonia)
The cost comparison is done for one staircase of previously described case study building and with following assumptions:
1) Cost of installing all necessary equipment;
2) Annual maintenance cost for all necessary equipment for whole staircase section;
3) Cost of heating supply air for one heating season assuming the Heating degree days for base indoor temperature of +21,0°C for Latvia 4263, for Estonia 5656 (8) and assuming that the heating occurs by district heating system with following costs - for Latvia 55.55 EUR/MWh; for Estonia 65 EUR/MWh;
4) Annual cost of all energy necessary to power the ventilation devices for whole staircase apartment assuming that they are powered by electricity with the cost of 0.169 EUR/kWh for Latvia; 0.15 EUR/kWh for Estonia.

## Slide 13: Life cycle cost analysis
Chart: Year
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Natural by opening windows and natural exhaust | 1800 | 9805 | 17810 | 25815 | 33820 | 41825 | 49830 | 57835 | 65840 | 73845 | 81850
Natural by having inlet valves and natural exhaust | 11100 | 19405 | 27710 | 36015 | 44320 | 52625 | 60930 | 69235 | 77540 | 85845 | 94150
Hybrid by having inlet devices in walls and mechanical exhaust | 15750 | 25360 | 34970 | 44580 | 54190 | 63800 | 73410 | 83020 | 92630 | 102240 | 111850
Decentralized mechanical supply and exhaust with heat recovery (room based system) | 76800 | 79685 | 82570 | 85455 | 88340 | 91225 | 94110 | 96995 | 99880 | 102765 | 105650
Decentralized mechanical supply and exhaust with heat recovery (apartment based) | 87000 | 92705 | 98410 | 104115 | 109820 | 115525 | 121230 | 126935 | 132640 | 138345 | 144050
Centralized mechanical supply and exhaust with heat recovery | 16760 | 21430 | 26100 | 30770 | 35440 | 40110 | 44780 | 49450 | 54120 | 58790 | 63460

## Slide 14: Comparison of ventilation systems
Type of ventilation system |  | Advantages | Disadvantages
Windows opening and natural exhaust |  | Low investments and maintenance Does not involve any technologies (solid) Easily controllable Does not affect architecture | Incoming air does not heat up therefore causing draft Incoming air does not go through filters therefore letting insects and dust Low control options Requires human interaction Very low working efficiency during warm period of year Let’s through extra noise from outside No possibilities for heat recovery Affected by outside weather (wind, temperature)
Natural ventilation with inlet valves |  | Relatively low investments and maintenance Requires only some equipment Easily controllable Incoming air goes through filters therefore not letting insects and dust inside Moderate control options | Incoming air does not heat up therefore causing draft (can be solved by placing inlet valves behind radiators) Requires some human interaction Very low working efficiency during warm period of year Let’s through extra noise from outside No possibilities for heat recovery Affects building façade by requiring openings
Mechanical exhaust ventilation with natural supply through inlet valves |  | Relatively low investments and maintenance Requires only some equipment Easily controllable Incoming air goes through filters therefore not letting insects and dust inside The exhaust fans can be equipped with light switch or moisture sensor Stable working throughout the year | Incoming air does not heat up therefore causing draft (can be solved by placing inlet valves behind radiators) Let’s through extra noise from outside Low possibilities for heat recovery Affects building façade by requiring openings
Mechanical supply-exhaust ventilation | Room based | Requires only some equipment High control options Incoming air goes through filters therefore not letting insects and dust inside The devices can be equipped with moisture sensor Stable working throughout the year With heat recovery therefore reducing heating costs and supplying warm air | Very high investment costs Let’s through extra noise from outside and is a source of noise (relatively quiet) Affects building façade by requiring openings Low air volumes Requires multiple devices for each apartment
 | Apartment based | All-in-one equipment includes all necessary parts Complete control options Incoming air goes through filters therefore not letting insects and dust inside The devices can be equipped with moisture, CO2, VOC or occupancy sensors Stable working throughout the year With heat recovery therefore reducing heating costs and supplying warm air | Very high investment costs Can be a source of noise if designed incorrectly Requires place for ducts in shafts and rooms
 | Building based | All-in-one equipment includes all necessary parts Average investment costs High control options Incoming air goes through filters therefore not letting insects and dust inside The device can be equipped with moisture, CO2 occupancy sensors Stable working throughout the year With heat recovery therefore reducing heating costs and supplying warm air | Occupants are not in control of the centralized device Can be a source of noise if designed incorrectly Requires place for ducts in shafts, building envelope and rooms

## Slide 15: Integrated duct design
Fig. 4. Integration of ducts into prefabricated panel (approx. thermal transmittance is 0.18 W/(m2·K))
Velocity in ducts | Round duct size, mm |  |  | 
 | Latvia (140 m3/h) | Estonia (119 m3/h) | Denmark (50 m3/h) | Portugal (135 m3/h)
<3 m/s | 160 | 125 | 100 | 160
< 4m/s | 125 | 125 | 100 | 125
< 6m/s | 100 | 100 | 100 | 100

## Slide 16: HVAC systems “house engine”
Typical components of modular HVAC unit are:
Heat exchanger for heating loop;
Hot water heat exchanger;
Local energy source (gas boiler, heat pump, connection to external energy sources);
Expansion tank;
Air handling unit including ventilation heat recovery;
In rarer case also cooling source.
house engine
Thermal energy production unit
Ventilation unit
Thermal energy storage
Renewable energy
Gas boiler
Heat pump
Wood pellet boiler
Hot water storage tank
Heating tank
PV panels
Solar thermal collectors
Heat recovery
Wind energy

## Slide 17: HVAC systems “house engine”
Example of “engines” in Estonian pilot:
  Ventilation
    ½ building based balanced ventilation units with VHR
      „engine“ on roof,
      ducts in modular panel
    ½ apartment based balanced ventilation units with VHR
      „engine“ in balcony or in coatroom
      ducts trough modular panel
pos. | neg
Ventilation is always on | Difficult to control
Quiet | Kitchen without VHR
Less disturbance of the residents. | 
pos. | neg
Advanced control | Risk for higher noise
Kitchen with VHR | More ducts in apartment
Higher efficency of VHR | 

## Slide 18: Practicla exercise
To choose, calculate and design ventilation systems for given building:
Determine the necessary ventilation rate for each premise;
Design the ventilation system;
Make a rough cost estimate of designed system;
Perform Life cycle cost analysis for chosen ventilation system.
Initial data:
  Building plans;
  Location of building.